SECTION 01 35 33
INFECTION CONTROL RISK ASSESSMENT (ICRA) PROJECT REQUIREMENTS

This section is required for ALL University Iowa Health Care projects and shall be edited by the Design Professional.

The Design Professional shall develop an approved detailed Interim Infection Control Measures plan for the Work areas, including enclosure placement, enclosure construction, HVAC isolation details, and Negative Air Machine requirements for inclusion in the Construction Documents.  This IICM plan must be presented to and approved by the University Iowa Health Care Infection Control Risk Assessment (ICRA) Committee prior to advertisement for bid.

The Design Professional shall coordinate demolition and construction activities in adjacent areas, especially where access to ceiling areas is required.

When there is a need for Work outside of the Primary Containment Area, the Design Professional shall denote the area(s) as Secondary Containment Areas with the proper ICRA Class identified for all Containment Areas on the Drawings.

The ICRA Committee and Owner’s Rep should always be made aware of situations where the Negative Air Machine cannot be exhausted to outside of the building envelope.

All Negative Air Machine requirement calculations shall be done by the Design Professional and inserted into this Specification prior to issuing Construction Documents for Bid. (See Part 3 herein)]

PART 1 - GENERAL

  - DEFINITIONS

    - Airborne Contaminants include dust, smoke and fumes and Airborne Contaminant producing activities include, but are not limited to:

      - Demolition and/or removal of walls, floors, ceilings, and other finish materials.

      - Demolition of plumbing, mechanical and electrical systems and equipment.

      - Finish operations such as sanding, painting, and application of special surface coatings.

      - All other construction activity that may generate dust, smoke, or fumes.

    - Containment Area: A Primary and/or Secondary Containment Area.

    - High Efficiency Particulate Air (HEPA): A HEPA filter is an air filter capable of capturing 99.97% of particles passing through the filter that are 0.3 microns.

    - Interim Infection Control Measures (IICM): A detailed plan outlined by the Contract Documents to ensure proper enclosure placement, enclosure construction, HVAC isolation details, and Negative Air Machine quantity and sizing.

    - Negative Air Machine: A freestanding, portable device that creates Negative Air Pressure.  It does so by removing air via flexible ductwork from the Containment Area.  The units can also be placed remotely from the Containment Area and use ductwork to remove air from the controlled environment.

    - Negative Air Pressure: The relative air pressure difference between two areas in a facility.  A space that is at negative pressure has a lower pressure than adjacent areas, ensuring that any directional air movement is from the clean air environment into the contained area and preventing contaminated air from escaping into adjacent rooms or areas through doors, openings, and cracks.

    - Portable Air Scrubber: HEPA filter equipped air circulation (non-ducted) machine that provide roughing filters (stage 1 pre-filter), primary filters (stage 2 pre-filters) and HEPA final filters, and will clearly indicate airflow capacity, to permit the Responsible Person to easily calculate and record the Air Change Rate for the work area. A minimum of 6 air exchanges per hour are required (for recirculating option only). If negative pressure is achieved with less than the required Portable Air Scrubbers, remaining air scrubbers will be used as recirculating machines. Safety features will include thermal overload protection, auto reset and UL compliance rating. Charcoal filter may be desired to decrease odors. Annual inspection of scrubbers is required.

    - Preparation Area (aka Anteroom): A specific area designated by the Owner for donning and removing protective clothing prior to enter the Primary Containment Area.

    - Primary Containment Area: The largest area of project work around which infection control (dust) enclosures are built.

    - Protection Areas: Interior occupied areas within the facility, that are adjacent to a Primary Containment Area, either occupied or used for passage, as well as areas connected to construction area by mechanical system air intake, exhaust, and ductwork.

    - Secondary Containment Area: Areas of Work within the Protection Area outside of the Primary Containment Area that require a form of dust control.

  - CONSTRUCTOR’S RESPONSIBILITY

    - Constructor shall provide all enclosures necessary to separate all construction activities from non-construction areas of the hospital.

    - Constructor shall provide and maintain all necessary enclosures required to create Primary and Secondary Containment Areas required to perform the Work.

    - Constructor shall verify the maintenance of Negative Air Pressure in Primary and Secondary Containment Areas relative to Protection Areas on a continual basis by use of differential pressure monitors.

    - Constructor shall comply with applicable codes and use installation procedures and methods that satisfy applicable code requirements and procedures.

    - All new ductwork and duct accessories openings to be incorporated into the project shall be blocked off or sealed to keep them clean before arriving to the project site.

    - Constructor shall hire a testing and balancing firm to verify air flow of Negative Air Machines required by the Contract Documents and submitted to the Owner.

    - Constructor is responsible for its personnel’s education and certification and for the Above Ceiling Work Permit preparation required to perform Work:

      - Above Ceiling Work Education and Certification, information found at UIHC Above Ceiling Work Policy

      - General Above Ceiling Work Permit found at UIHC Above Ceiling Permit

      - Failure to comply with Above Ceiling Work Permit requirements will result in immediate stoppage of Work.

    - Constructor is responsible for preparing, maintaining, and providing to the Owner the following documents at the intervals indicated on the documents and for the entire duration of the project:

      - Negative Air Machine log (as applicable),

      - University Iowa Health Care Life Safety/Interim Life Safety Measures Evaluation and Amendment Record, and

      - Daily Infection Control/Life Safety Risk Assessment Checklist for use During Construction and Renovation.

These documents are found at  https://www.facilities.uiowa.edu/projects/contractors.

    - Constructor shall not track any type of dust, debris or foreign material from their Work sites.

    - Constructor shall have proper Interim Infectious Control Measures (IICM) in place prior to commencement of Work.  This includes but is not limited to having walk off mats, Portable Air Scrubbers, Negative Air Machines and requirements in place.

    - If the Constructor fails to maintain Infection Control Risk Assessment Project Requirements:

      - The Constructor shall correct non-conformance immediately.

      - If non-conformance issues are not corrected immediately, the Owner may stop Work as provided in Contract Documents at no additional cost to the Owner.

      - The Owner may dismiss Constructor’s job site personnel for non-conformance.

      - Costs to the Owner associated with non-conformance shall be assigned to the Constructor.

  - OWNER RESPONSIBILITIES

    - The Owner may provide baseline particle counts and conduct periodic air sampling of Protection Areas during construction to monitor effectiveness of Interim Infection Control Measures (IICM).

  - SUBMITTALS

[Submittal requirements for this specification section shall be identified as a line item on the submittal log at the end of specification section 01 33 23 – Submittals]

    - Constructor shall submit the following information:

      - Submit information for Constructor’s plan for containment of Airborne Contaminants and IICM for the Owner’s review and approval.

        - Drawings for each phase of the Work shall indicate, as a minimum, Primary and Secondary Containment Areas, Protection Areas, location of all IICM including but not limited to temporary enclosure and enclosure types, Anterooms, location of Negative Air Machines including vent/exhaust location, capped ductwork, and differential pressure monitors.

        - Negative Air Machine calculations based on Constructor verified Containment Area dimensions (volume).

      - Product Data: Submit data on specified Products (Materials) and include Manufacturer’s recommended interval for dust filter media changes for the Negative Air Machines and DOP testing results.

PART 2 – PRODUCTS

  - MATERIALS

    - HEPA Vacuums:

      - HEPA vacuum shall trap 99.999% of particles 0.12 microns and larger.

      - HEPA Vacuum shall have a minimum airflow of 90 cfm.

      - Acceptable products:

        - ISC Sales “Minuteman Model CRV- 99.999%”

        - Nilfisk Advance

        - Pro-Team “HEPA/ULPA Vacuum”

        - Or approved equal.

    - Polyethylene:

      - 6 mil or 8 mil thick reinforced laminated polyethylene film and shall meet requirements of NFPA 701 large scale flammability test and ASTM E84 Class A.

      - Include compatible fire-retardant tape.

      - Acceptable products:

        - AmeriCover “Surface Cover”

        - Reef Industries “Griffolyn Type 55 FR”

        - Or approved equal.

    - Adhesive-Faced Contamination Control Mats (sticky walk-of mats):

      - Size of mats shall be the width of the opening and 30” (minimum) depth.

      - Acceptable products:

        - ASG “Walk-off Mats”

        - Controlled Environment Equipment “Cleanline Sticky Mat”

        - Liberty Industries “Tacky Mat”

        - Curtain Wall Company “CleanStep” tacky mats

        - AmeriCover Sticky Mat Tacky Mats

        - Pro Tectii “Pro Tect Tacky Mats”

        - HD Supply Sticky Mat Dirt Trapper

        - Or approved equal.

    - Negative Air Machine:

      - Provide unit sized to meet room requirements.

      - Carbon filtering, when required.

      - Units shall include prefilters, primaryl filters, HEPA - filters and filter static pressure gauges.

      - HEPA filters shall be 99.97% efficient at 0.3-micron particle size.

      - Acceptable manufacturers:

        - Abatement Technologies

        - Phoenix

        - Dri-Eaz

        - Micro-Trap, Inc.

        - NIKRO Industries, Inc.

        - Advanced Containment Systems, Inc (ACSI)

        - Omnitec Design, Inc.

        - Or approved equal.

    - Portable Air Scrubber:

      - Provide unit sized to meet room requirements

      - Units shall include prefilters, primary filters and HEPA - filters

      - HEPA filters shall be 99.97% efficient at 0.3-micron particle size.

      - Acceptable manufacturers:

        - Abatement Technologies

        - Dri-Eaz

        - Advanced Containment Systems, Inc (ACSI)

        - Or approved equal.

    - Zipper Lock Entrance:

      - Fire retardant, reinforced vinyl construction with reinforced stitching.

      - Acceptable products:

        - Curtain Wall Company “Dust Door”

        - Pro Venture Inc. “Zip-Up”

        - Zip Wall Heavy Duty Zipper

        - Or approved equal.

    - Temporary Prefabricated Enclosure Units:

      - Provide the enclosure with an inspection window and pressure differential porthole and HEPA Vacuum.

      - Acceptable products:

        - Fiberlock Technologies “Kontrol Kube” with frame #6640, enclosure #6442, wheelbase platform #6443 and Milfish 87 cfm vacuum device and manometer.

        - Specialty Tool Manufacturing “MCU-Quick Wall Mobile Containment Unit”; provide with HEPA vacuum connection.

        - Mintie Technologies “ECU EnteRoom Envelope”

        - Or approved equal.

    - Airflow Direction Indicator:

      - Acceptable products:

        - Airflow Direction Inc. “ADI-69-V-N”

        - Austin Ventrues “Model LN102”

        - Or approved equal.

    - Dust Catching Device:

      - Disposable, dry, electrostatic cloths or mitts for dust removal.

      - Disposable, wet cloths, presoaked with cleaning solution, for dust removal.

      - Acceptable products:

        - Proctor & Gamble “Swiffer Dry”, “Swiffer Mitt” or “Swiffer Wet”

        - Reckitt Brenckiser “Mop & Glo”

        - S.C. Johnson & Sons “Pledge Grab It”

        - Or approved equal.

    - Magnehelic Differential Pressure Sensor

      - Dwyer #2000-00

        - Range 0 - 0.25” w.c.

        - Minor divisions 0.005

        - Calibrated for vertical scale position.

        - Or approved equal.

      - Active Pressure Monitor with Data Logging and Alarming Capabilities

        - Manufacturers as approved by Owner

    - Disposable Coveralls, Hair Nets, Beard Nets, Shoe Covers

      - Uline Products “Uline Deluxe”

      - Other acceptable manufacturers are:

        - 3M

        - DuPont

        - Enviroguard

        - Lakeland Industries, Inc.

        - Kimberly-Clark

        - Or approved equal.

PART 3 – EXECUTION

NOTE: The ICRA Committee shall determine which Interim Infection Control Measures Classification(s) to use on the project and the Design Professional shall insert the signed Infection Control Permit into this specification Part 3.

The ICRA permit can be found at UIHC ICRA Permit on the UI Facilities Management website.

END OF SECTION 01 35 33