SECTION 01 78 23

OPERATION AND MAINTENANCE MANUAL

PART 1 GENERAL

- SECTION INCLUDES

  - Format and content of Operation and Maintenance (O&M) Manuals.

  - Schedule of deliverables.

  - Requirements for training of Owner personnel.

- RELATED REQUIREMENTS

  - The following sections contain related requirements:

    - Section 01 33 23 - Submittals

    - Section 01 77 19 - Contract Closeout

    - Section 01 78 39 - As-Built Documents

    - Section 01 91 13 - MEP Commissioning

    - Section 01 91 23 – Building Envelope Commissioning

    - Specific product, equipment, and assembly technical sections.

  - Refer to ASHRAE Guideline 4 current edition for Standard of Care and definitions.

- GENERAL REQUIREMENTS

  - The O&M Manuals shall be organized as a practical, actionable guide to achieve the following:

    - Provide instructions for the safe, efficient, and sustainable use of the facility, system(s), assemblies, and component(s).

    - Provide the basis for training Owner personnel.

    - Provide the basis for establishing maintenance programs for optimal system(s), assemblies, and component(s) lifecycle.

    - Provide the technical information required for the maintenance, repair, etc. of system(s), assemblies, and component(s).

    - Provide a record of as-installed setpoints, sequences, and operating conditions of system(s), assemblies and component(s).

  - The following items are not to be included in the O&M Manual:

    - Warranties  	See Specification Section 01 77 19 – Contract Closeout

    - Submittals 	See Specification Section 01 33 23 – Submittals

    - Testing, Adjusting, and Balancing Report(s)

- O&M MANUAL CONTENT

  - O&M Manual shall include the following tabs:

    - Table of Contents Tab

      - Include all tab and section information.

    - System, Assembly, and Component Tab (Multiple tabs):

[NOTES TO DESIGN PROFESSIONAL:

Edit this list following review by: FM BLS Area Maintenance Manager, Public Safety Key & Access Security, UI Housing, Athletics, Rec Services, or UIHC Engineering Services, to establish systems and components to be included in the O&M Manual and the specific training requirements for each.

Include CSI Division reference for each selected system and/or component.  Do not rely solely on CSI Specification Numbers (08 11 13) or project specific equipment names (HX-1) for identification.]

      - Arrange contents by building system(s) and component(s).  Provide an individual tab for each system, assembly and component identified in this Section.

      - The following Specification sections shall have an individual tab within the O&M Manual. Owner may request edits to the following list based upon submittals and approval of systems, assemblies, and components:

        - Section ## ## ## - Interior Finishes, including Final Finish Schedule and Paint Formulas

        - Section ## ## ## - Ceiling Systems

        - Section ## ## ## - Flooring Systems

        - Section ## ## ## - Exterior Finishes, including Final Finish Schedule

        - Section ## ## ## - Casework and Furniture

        - Section ## ## ## - Roofing Systems, including Leak Detection Systems

        - Section ## ## ## - Firestopping Systems

        - Section ## ## ## - Doors and Hardware

        - Section ## ## ## - Windows and Operable Shades

        - Section ## ## ## - Glazing Systems

        - Section ## ## ## - Skylight/Sloped Glazing Systems

        - Section ## ## ## - Overhead Coiling Doors and Controls

        - Section ## ## ## - Flooring Systems

        - Section ## ## ## - Loading Dock Accessories

        - Section ## ## ## - Platforms and Lifts

        - Section ## ## ## - Elevators & Escalators

        - Section ## ## ## - Fire Suppression Systems and Fire Pumps

        - Section ## ## ## - Water Fountains and Central Water Fountain Systems, Controls, and Pumps

        - Section ## ## ## - Irrigation Systems

        - Section ## ## ## - Sump and Ejector Pumps and Controls

        - Section ## ## ## - Compressed Air Systems, including process air, systems/lab air, and any control air system or pneumatic control air.

        - Section ## ## ## - Domestic Water Pumps, Softeners, and Filtration

        - Section ## ## ## - Domestic Water Heaters and Controls

        - Section ## ## ## - Specialty Plumbing Fixtures and Trim such as hands-free faucets/controls/batteries

        - Section ## ## ## - Building Controls including component locations

        - Section ## ## ## - Hydronic Pumps

        - Section ## ## ## - Hydronic Heat Exchangers, Filtration, and Chemical Feed Systems

        - Section ## ## ## - In-Slab Hydronic Systems

        - Section ## ## ## - Snow Melt and Glycol systems

        - Section ## ## ## - Fire Dampers/Smoke Evacuation Systems

        - Section ## ## ## - Fan Coil Units

        - Section ## ## ## - Central vacuum pump systems and Controls

        - Section ## ## ## - Chilled Water and Off-Season Chilled Water Systems

        - Section ## ## ## - Deionizing or RO Water Systems

        - Section ## ## ## - Boilers and Controls

        - Section ## ## ## - Steam Systems and Specialty Steam Equipment

        - Section ## ## ## - Air Curtains

        - Section ## ## ## - Exhaust Fans including HVAC, Kitchen and Restroom Systems

        - Section ## ## ## - Air Handling Systems

        - Section ## ## ## - Specialized ventilations systems such as Art/Archive Storage, Processing, or Environmental Safety Systems.

        - Section ## ## ## - Humidification or Dehumidification Systems and Controls

        - Section ## ## ## - Overcurrent Coordination, Arch Flash, Short Circuit Studies

        - Section ## ## ## - Electrical Power Monitoring

        - Section ## ## ## - Occupancy Sensors for lighting and HVAC controls

        - Section ## ## ## - Lighting Fixtures

        - Section ## ## ## - Lighting Controls, Daylight Harvesting and Dimming Systems

        - Section ## ## ## - Emergency Power Systems including Generators, controls and transfer gear.

        - Section ## ## ## - Access Controls

        - Section ## ## ## - Fire Alarm, Detection and Sampling Systems

        - Section ## ## ## - Utilities – Mechanical Systems and Distribution

        - Section ## ## ## - Utilities – Electrical Systems and Distribution

        - Section ## ## ## - VFDs

        - Section ## ## ## - Building Automation Systems

        - Section ## ## ## - Other

- SYSTEM, ASSEMBLY AND COMPONENT TAB CONTENT

  - Each system, assembly, and component tab shall include the information outlined below:

    - General Information Section

      - System, assembly, and component designation (per Contract Documents).

      - Component (product) CSI number.

      - Component (product) nameplate data:

- Manufacturer

- Model number

- Serial number

- Size

- Horsepower

- Voltage and amperage

      - Location within facility (i.e. room).

      - Installation contractor contact information with phone number.

      - Emergency or service contact Information with phone number.

      - Customer service and parts contact information with phone number and website.

    - Sequence of Operations Section

      - As-installed narratives and Sequence of Operations for:

- Normal/auto operations mode

- Manual/non-auto operations mode

- Fail/emergency operations mode

      - As-installed Control(s) diagrams

- Daylight Operations Mode

    - Constructor Testing and Training Section

      - Manufacturer’s Startup Reports

      - Functional Test Reports

      - Training Materials

    - Component (Product) Operations AND Maintenance Information Section

      - Manufacturer’s installation instructions.

      - Manufacturer’s startup and troubleshooting instructions

      - Manufacturer’s technical instructions

      - Manufacturer’s operations instructions

      - Performance data, rating, and curves

      - Parts list (Special tools and maintenance equipment)

      - Wiring diagrams (if applicable)

      - Valve Schedule

      - Preventative Maintenance schedule recommendations

      - Manufacturer’s lubrication schedule and list of acceptable lubricants

      - Manufacturer’s care and cleaning instructions

- O&M MANUAL FORMAT

  - Electronic Format

    - Electronic file shall be searchable, fully bookmarked .pdf.

      - Bookmark the .pdf file by tabs listed under Section 1.4 sub-bookmark system and component tab by section as listed under Section 1.5.

      - Electronic file label shall include the following:

- University of Iowa Project Number and Name

- Contractor Name

- O&M Manual

- Volume # of #File name shall be as follows

Example: 0719201-Acme Contractors-O&M Manual-Vol1of3.pdf

- O&M MANUAL DELIVERABLES

  - 50% Construction O&M Manual Deliverable:

    - The Contractor shall submit to the Design Professional an electronic copy of the 50% Construction O&M Manual(s) prior to submission of its pay application requesting payment of 50% of the Contract value or more.

    - Payments beyond 50% of the contract amount may be withheld until the 50% Construction O&M Manuals are reviewed and accepted by the Owner.

    - The requirements for the 50% Construction O&M Manual shall have:

      - Table of contents tab

      - System, assembly, and component tab(s) shall be 100% complete:

- Article 1.5, Section 1

- Article 1.5, Section 4

  - Final O&M Manual Deliverable:

    - Prior to Final Completion, the Contractor shall submit an electronic copy of the Final O & M Manual to the Design Professional for review via BuildUI.

    - Following Design Professional’s review, O&M manuals will be returned to Contractor for one of the following:

      - If Design Professional marks the action as reviewed – No further action required.

      - If Design Professional marks the action as revise and resubmit – Contractor shall revise and resubmit via BuildUI for Design Professional’s review until the Design Professional marks the action as reviewed.

    - The Final O&M Manual shall have:

      - Table of contents tab

      - System, assembly, and component tabs

- Article 1.5, Section 1

- Article 1.5, Section 2

- Article 1.5, Section 3

      - DDC temperature control drawings (See Article 1.5, Section 5 above):

- The Contractor shall submit one (1) copy of AutoCAD/Visio editable files for all "As-Installed" control drawings indicated below:

          - Control drawings with detailed piping and wiring diagrams, bill of material and Sequence of Operation for each system, including interfaces with equipment manufacturers, and other suppliers of equipment and systems.

          - I/O panel layouts and terminations along with interface panel drawings.

          - Valve and Damper Schedules showing size configuration, capacity, failure position and location of all equipment.

          - Individual data sheets for each control and automation system components.

          - Termination and Ladder wiring diagrams.

          - Small-scale site and equipment drawings showing the control component locations in occupied space, equipment rooms, mechanical equipment, etc.

          - Contractor shall provide Owner one (1) set of red line as-installed Drawings showing actual locations of master controllers, system control panels, and Variable Frequency Drives.

            - Drawings should also include routing of control communication bus and pneumatic piping.

            - Include riser diagrams with intended routing of communications and power.

            - Include controller addresses/serial numbers and area/room served on these same riser diagrams.

            - As-installed drawings shall incorporate the actual routing as a completed document.

      - DDC Sequence of Operation:  A detailed sequence of operation describing exact method of control shall be included on the automation system components flow diagram.

- TRAINING OF OWNER’S PERSONNEL

  - Scheduling and Coordination:

    - All Owner training shall be completed prior to Substantial Completion.

    - Contractor shall submit proposed training schedule to Owner a minimum of 60 days prior to Substantial Completion.  Contractor’s proposed training schedule shall include the following:

      - Proposed dates for training by system, assembly, and component.

      - Location of proposed training; classroom or onsite.

      - Name, position, and profile of trainer.

      - Detailed agenda and syllabus for training sessions

      - Specific skills or knowledge the Owner’s Personnel is expected to master.

    - Training schedule shall be adjusted as required to minimize disruption to Owner’s operations.  Provide training sessions outside of normal working hours as required for Owner’s personnel.

  - Training Content:

    - Refer to technical Specification sections for additional training requirements.

    - O&M Manual shall be used as the basis for instruction.

    - Prior to Substantial Completion, provide the Owner all specialty tools, keys, pass codes, or other items required for the operation or maintenance of systems, assemblies, and components.

    - Each training session shall include a thorough review of the following, as applicable:

      - General Information Article 1.5

      - Operations information

- Overview of systems, assembles, and components including primary and secondary functions, as-installed sequence of operations, area served, and system limitations.

- Standard operating procedures for

          - Normal systems, assemblies, and components startup and shutdown.

          - Normal, manual, and automatic operations.

          - Seasonal, intermittent, or non-occupied operations.

          - Emergency or failure conditions including the meaning of warning, trouble, and error messages.

        - Special tools and maintenance equipment.

        - Startup and troubleshooting instructions.

      - Maintenance Information

- Maintenance information Section 1.5

- Component access.

- Alignment, tension, vibration, and noise criteria and adjustments.

END OF SECTION

| Notes: - BLS/UIU to be invited to all first installations and equipment startups as optional attendees for GEF facilities. - UI Housing and Dining to be invited to all first installations and equipment startups as optional attendees for Residence Hall facilities. - UIHC to be invited to all first installations and equipment startups as optional attendees for UIHC facilities. |  | Training By: IC: Installing Contractor DP: Design Professional MR: Manufacturer’s Rep MT: Manufacturer’s Engineer or Service Tech | Trainees: AM: Area Mechanic ESM: Environmental Systems Mechanic PF: Pipe Fitters EC: Electricians FS: Fire Safety US: User Staff CS: Custodial Staff UIU: University of Iowa Utilities / ENGIE UIHC: Engineering Services |
| --- | --- | --- | --- |
| Specification Section and Component/System/Assembly | (Number and) Minimum Length of each session in Hrs. | Training Conducted by | Trainees |
| Section ## ## ## - Coiling Doors | 2 | MR | AM, US |
| Section ## ## ## - Food Service Equipment | 4 | IC, MR | AM, US |
| Section ## ## ## - Elevators | 4 | IC | AM, EC |
| Section ## ## ## - Fire Suppression | 2 | IC | AM, PF, FS |
| Section ## ## ## - Sensor Faucets and Flush Valves | 2 | IC, MR | AM, PF |
| Section ## ## ## - Sump Pump Controls | 2 | MR | AM, PF |
| Section ## ## ## - Compressed Air Systems | 2 | MT | AM, ESM, PF |
| Section ## ## ## - Controls | (2) 4 [60 days between sessions] | IC | AM, ESM, UIU |
| Section ## ## ## - Snow Melt | (2) 2 [At Seasonal change] | MT | AM, ESM, EC |
| Section ## ## ## - Chilled, Hydronic, and Steam Flow Diagrams | 4 | IC, DP | AM, ESM, PF |
| Section ## ## ## - Humidifiers | 2 | IC, MT | AM, ESM, PF |
| Section ## ## ## - AHUs and associated systems | 4 | IC, MR | AM, ESM, PF |
| Section ## ## ## - Dewatering System | (2) 2 | IC, MR | AM, ESM, PF, EC, UIU |
| Section ## ## ## - Generator and Transfer systems | (2) 2 | IC, MT | AM, ESM, EC, UIU |
| Section ## ## ## - Lighting Controls: Daylight harvesting, software, hardware | (2) 4 | IC, MT | AM, EC |
| Section ## ## ## - Specialty Lighting, Ballasts, Lamps | (2) 2 | MR | AM, EC |
| Section ## ## ## - Lighting Fixtures Re-lamping and cleaning | 2 | IC | CS |
| Section ## ## ## - VFD Maintenance and Programming | (2) 4 | MT | AM, ESM, EC |
| Section ## ## ## - Life Safety – Fire Alarm/Fire Protection | 2 | IC | AM, FS |
| Section ## ## ## - Lab Gasses | 2 | IC | AM, ESM, PF, US |
| Section ## ## ## - Lab Controls | (2) 2 | IC, MT | AM, ESM, EC, US |
| Section ## ## ## - Site Utility Distribution – Flow Diagrams and Component Locations | 4 | IC, DP | UIU |
| Section ## ## ## - Flooring System Repair and Maintenance | 2 | IC | CS |
| Section ## ## ## - Fire Alarm Systems | 4 | IC | AM, FS |
| Section ## ## ## - Fire Protection Systems | 4 | IC | AM, FS |
| Section ## ## ## - Audio Visual (A/V) Systems | 4 | IC | AM, US |
| Section ## ## ## - Fire Shutters | 2 | IC, MR | AM, FS, UIHC |