SECTION 01 91 23

BUILDING ENVELOPE COMMISSIONING (BECx)

PART I GENERAL

- SECTION INCLUDES

  - Commissioning objectives.

  - Roles and responsibilities.

  - Installation verification and functional performance testing requirements.

  - Systems to be commissioned.

- RELATED REQUIREMENTS

  - The following sections contain commissioning-related activities and requirements:

    - Section 01 33 23 - Submittals

    - Section 01 77 19 - Contract Closeout

    - Section 01 78 23 - Operating and Maintenance Manual

    - Section 01 78 39 - As Built Documents

    - Specific Product, Component, and Assembly Technical Specification Sections.

  - Refer to ASTM E2813, ASHRAE Guideline 0-2013 and NIBS Guideline 3-2012 for commissioning process overview, standard of care, and definitions.

- BECx OBJECTIVES

  - The primary function of BECx is to serve as the Owner's quality assurance program pertaining to the materials, systems, and assemblies that provide shelter and environmental separation between environmentally distinct spaces.

  - The BECx shall review and observe the following areas of emphasis: 1) transitions between building envelope assemblies, 2) transitions between and within compass elevations, and 3) changes in direction.

  - The BECx shall also review and observe continuity of the assemblies and ensure the following general assemblies are protected from physical damage: 1) air barriers, thermal barriers, vapor barriers, and moisture barriers.

  - The BECx process is not a substitute for the Constructor’s installers' quality control procedures and does not diminish or subtract from their responsibility to provide a finished and fully functioning Control Barrier assembly in accordance with the Contract Documents.

- BECx ROLES AND RESPONSIBILITIES

  - OWNER’S BUILDING ENVELOPE COMMISSIONING AGENT (BECxA)

    - The Owner shall retain the BECxA to lead the BECx effort and to perform reviews of the Control Barriers.

    - The primary role of the BECxA shall be to develop and coordinate the execution of the Owner's Quality Assurance Program pertaining to the materials, systems, and assemblies that provide shelter and environmental separation between environmentally distinct spaces.

    - The BECxA shall observe, document, and provide its professional opinion as to whether materials, systems, and assemblies are installed and functioning in accordance with the Contract Documents and manufacturer’s recommendations.

    - BECxA shall attend planning and job-site meetings to obtain information on construction progress as requested by the Owner.

    - The BECxA shall review Submittals for the purposes of preparing and/or refining the Construction Checklists and Functional Performance Testing procedures and to provide comments to the Owner and Design Professional of a technical nature as appropriate.

    - BECxA shall perform periodic construction observation review of Constructors' efforts, for evaluation of workmanship, functional installation, and material, system, and assembly performance. These observations shall be made at milestone activities, including but not limited to Mock-ups, commencement of assembly installations, randomly scheduled site reviews, and testing.

    - The BECxA shall assist in identifying potential solutions to non-conforming work. Final resolution shall remain the responsibility of the Constructor.  Refer to NIBS 3-2012 and/or ASTM E2813 for acceptable standard of care.

  - CONSTRUCTOR’S COMMISSIONING COORDINATOR (CCxC)

    - The Constructor shall designate prior to the BECx Kickoff Meeting one experienced individual to serve as the CCxC with full authority to direct work, [Edit this section as required by scope/complexity of the project] separate from the Constructor’s superintendent or project manager.  The Owner’s Representative shall have final approval of the proposed CCxC.

    - The CCxC is responsible for planning, scheduling, coordinating, conducting, and verifying all BECx activities required by the Contract Documents, ensuring that all materials, systems, and assemblies are complete and performing to the Contract requirements.

    - The CCxC shall provide and maintain a Constructor Quality Control Plan which shall clearly indicate the Constructor’s strategy and method for ensuring coordination of building envelope Subcontractors, construction sequencing, and Submittal conflict management.

    - The CCxC shall communicate and coordinate with the Owner’s Representative, the  BECxA, and the building envelope Subcontractors to schedule and execute the BECx process, including Construction Checklists, Functional Performance Testing, and other activities described in the Contract Documents or as requested by the BECxA.

    - The CCxC shall keep the Owner’s Representative, BECxA, and Design Professional informed of the progress of construction and status of the installation of commissioned materials, systems, and assemblies.  This shall be accomplished, in part, by the Constructor providing a Two-Week Building Envelope Look-Ahead Schedule separate from the Constructor’s required master construction schedule(s).

    - The CCxC shall review material, system, and assembly Submittals to be commissioned for apparent completeness prior to the Constructor’s submission for formal review.

    - The CCxC (with collaboration of the BECxA) shall conduct regular on-site BECx coordination meetings with the Design Professional, Owner’s Representative, BECxA, and all building envelope Subcontractors.  The purpose of these meetings shall be to coordinate schedule, discuss work sequence, and determine deficiency resolution. These meetings shall be independent from the regularly scheduled construction progress meetings.

    - The CCxC shall prepare and distribute all BECx meeting minutes.

  - CONSTRUCTOR'S ADDITIONAL ROLES AND RESPONSIBILITIES

    - The Constructor shall provide all labor, supervision, materials, tools, equipment, and other services, as necessary, to complete the required installation of materials, systems, and assemblies in accordance with the Contract Documents and manufacturer’s recommendations.

    - The Constructor shall ensure all material, system, and assembly warranty requirements are followed and shall ensure all adjacent materials, system and assembly components are compatible.

    - The Constructor shall coordinate, manage, and ensure completion of all BECx documentation.

    - The Constructor shall provide the following to the BECxA upon request: [Edit highlighted sections below as required by scope/complexity of the project]

      - Submittals and other documentation requested as deemed necessary,

      - manufacturer acceptance of the individual installers and/or parent company,

      - BECx certificate(s) of completion, certifying that exterior enclosure materials, systems and assemblies are complete and ready for testing,

      - corrective action responses to the BECx Action Item Log within two (2) business days of receipt, and

      - photographs of installations, in-process and completed.

    - With input from the BECxA, the Constructor shall integrate BECx activities into its master construction schedule prior to the installation of any commissioned building envelope materials, systems, or assemblies. Each assembly or component to be commissioned shall be identified separately on the Constructor’s schedule.  At a minimum, the schedule shall identify the following activities and milestones and shall incorporate the BECxA scheduled site visits, [Enter # of visits based on the project complexity and schedule] fifty-two (52) visits, for review and testing:

              - BECx progress meetings - regular monthly meetings during installation of the primary building envelope material, systems, and assemblies,

              - BECx materials, systems, and assembly pre-installation meetings,

              - "First work" and completion of each building envelope assembly installation; including mockup(s) as applicable to the Project,

              - Owner training per Specification Section 01 78 23 - Operating and Maintenance Manual,

              - Building envelope material, systems, and assembly completion date(s), and

              - Building envelope warranty walkthrough date ten months following the Project’s Substantial Completion.

PART 2 PRODUCTS

  - TEST EQUIPMENT

  - The Constructor shall provide all test equipment required for Constructor to pre-test any materials, systems, and assemblies. (See Construction Checklist to determine if pre-test is required by Contract Documents.)

  - The BECxA shall provide all specialized test equipment required for Functional Performance Testing to be performed by the BECxA or their Testing Agent.

PART 3 EXECUTION

- SYSTEMS TO BE COMMISSIONED [NOTE TO SPECIFIER: Edit this section for specific project requirements.]

- Building Envelope Materials, Systems and Assemblies to be Commissioned: [Edit when systems are finalized] Bolded items below indicate primary systems for the purpose of BECx progress meetings.

  - Waterproofing (07 14 00, 07 14 13, 07 18 00)

  - Slab on grade vapor barrier (07 26 13)

  - Roof systems (07 54 19)

  - Roof Accessories (07 7 200)

  - Flashing, trim (07 62 00)

  - Air Barriers (07 27 00)

  - Exterior Insulation (07 21 00)

  - Exterior walls (07 42 13, 07 42 14, 07 42 64, 08 88 13)

  - Curtain walls, windows, storefronts, & glazing (08 43 13, 08 44 13, 08 44 26, 08 56 55, 08 80 00)

  - Doors (08 11 13)

  - Sealants (07 92 00)

  - Connection to existing building (07 95 00)

  - Louvers (08 91 00)

- BECx PROCESS

  - Within sixty (60 days) [Edit based on project scope/complexity] of Contract Award, the BECxA shall schedule and conduct a commissioning kickoff meeting to be attended by the Design Professional, Owner’s Representative, CCxC, Constructor, and building envelope Subcontractors of items to be commissioned. The purpose of the meeting is to review commissioning requirements, procedures, documentation, and scheduling of the Work.

  - CCxC shall submit their building envelope specific Quality Control Plan within ninety (90) days [Edit based on project scope/complexity] of Contract Award  which shall clearly indicate the Constructor’s strategy and method for ensuring coordination of building envelope Subcontractors, construction sequencing, and Submittal conflict management.  First Works and Mockup(s) and Pre-installation meetings shall be clearly identified.

  - Constructor shall submit product data, coordinated system and/or assembly shop drawings, and other requested documentation per Specification Section 01 33 23 - Submittals. CCxC review of Submittals shall be conducted prior to submission to the Owner, BECxA and Design Professional.

  - BECxA shall perform reviews of the building envelope Submittals and supplemental documentation, focusing on the continuity, constructability, compatibility, and sequencing of Control Barriers.

  - BECxA shall participate in two (2) [Edit based on project scope/complexity] building envelope coordination meeting(s) for materials, systems, and assemblies to be commissioned. The meeting shall be to review the coordinated shop drawings and special details indicating assembly integration into adjacent construction as compared to the Contract Documents, but shall also include the following:

    - confirmation of parent company and installer qualifications or certifications,

    - confirmation of complete approved product submittals,

    - review of First Works and Mockup schedule, installation sequence, and testing as applicable,

    - review of BECx Construction Checklist and manufacturer installation instructions,

    - review of installation limitations, i.e. Weather, Adjacent Construction, and Storage,

    - review of Functional Performance Testing procedures, including Constructor, building envelope Subcontractor(s) and manufacturer representative reviews and documentation.

    - review of main project Installation sequence and schedule,

    - in-person participation shall be required of the Owner, Design Professional, BECxA, CCxC, Constructor’s and/or building envelope’s Subcontractor’s project manager and lead installer, and others as requested by the Owner.

    - Manufacturer(s) technical representative, Constructor’s and/or building envelope Subcontractor’s testing agency representative (if applicable), adjacent impacted Subcontractor(s) shall be available by conference call.

  - The BECxA shall assist in resolving any issues identified during regular site inspections. The total number of contacted site visits by the BECxA is fifty-two (52) and shall start at the onset of foundation installation. [Edit the highlighted sections based on the project complexity and schedule.]

    - Six (6) site inspections shall be used specifically for review of waterproofing and under slab vapor barrier.

    - The remaining forty-six (46) site visits shall be used weekly during the installation of the primary building envelope material, systems, and assemblies above grade.

    - Breaks in the weekly site visits shall be at the coordinated discretion of the Owner and BECxA.

  - The BECxA shall review Request for Information (RFI) and Instruction to Constructor (ITC) at the request of the Owner as it relates to the impact on building envelope commissioning and the Owner Project Requirements.

  - The Constructor and building envelope Subcontractors shall complete the Construction Checklists and any additional testing requirements found in the Contract Documents.

  - CCxC shall review the Constructor’s and building envelope Subcontractor’s Construction Checklists (which may require the Constructor to perform pre-testing) for completeness and verify that all documentation requirements have been met.

  - BECxA shall review the project Testing Matrix and the Constructor’s Quality Control Plan with the CCxC to ensure all testing is identified and scheduled within the Contract Time requirements.

  - After confirming building envelope materials, systems and assemblies were installed correctly and the Construction Checklist(s) have been completed, including all required pre-test, and submitted to the BECxA; the CCxC shall coordinate Functional Performance Testing requirements with the BECxA.

  - The BECxA shall perform and witness Functional Performance Testing.

  - Materials, systems, and assemblies which fail to meet the Functional Performance Testing, Contract Documents, or manufacturer requirements shall be corrected by the Constructor and retested at no additional cost to the Owner.

  - CCxC shall coordinate manufacturer warranty relevant site visits with the BECxA and Owner.

- BECx CONSTRUCTION CHECKLISTS

  - The objective of the BECx Construction Checklists is to verify and document that the materials, systems, and assemblies are installed in accordance with the manufacturer’s instructions and Contract Documents.  See sample Construction Checklist, attached at the end of this section.

  - The Construction Checklists shall capture the following:

    - date and environmental conditions during installation,

    - materials, systems and assembly components and available batch dates,

    - manufacturer recommended preparation and installation requirements,

    - the day’s installation and competent responsible personnel, and

    - applicable comments and signatures.

  - The BECxA shall create Construction Checklists after the product data and/or shop drawings have been submitted and reviewed.

    - BECxA shall review the submittal data and prepare final Construction Checklists and Functional Performance Testing Procedures incorporating manufacturer requirements.

    - BECxA shall provide Checklists to Constructor after product submittal approval and prior to installation of the commissioned component.

  - The installing Subcontractor shall complete the Construction Checklists daily during the course of assembly and component installation and not as an activity at the end of the project.  The Construction Checklists shall certify the individual verification items have been performed, reviewed, and found to be complete for all assemblies and components.

  - The Construction Checklists for a given assembly must be successfully completed prior to its review of testing.  By completing and submitting the Construction Checklists, the CCxC confirms that the assembly and components are properly installed and ready for BECxA review and functional performance testing.

  - The Construction Checklists may be in addition to other testing and verification required elsewhere in the Contract Documents.

- FUNCTIONAL PERFORMANCE TESTING

  - See BECx Testing Matrix attached at the end of this section.

  - The objective of inspections and functional performance testing is to demonstrate and document that assemblies and components are installed and perform in accordance with the Contract Documents.

  - The BECxA shall prepare or approve Functional Performance Testing procedures based on the system sequences of operation and the manufacturer's product data.

  - The BECxA shall witness and document any Functional Performance Testing performed by the Constructor.

  - The Constructor shall provide the BECxA assistance as needed to complete the Functional Performance Testing, including, but not limited to, providing access to equipment and components, including the use of ladders, lifts, scaffolding and platforms, operators, support personnel, Personal Protective Equipment, removal and replacement of finishes, etc.

  - The BECxA shall inspect and/or test a representative sample area of each assembly and component, with emphasis on the interface of adjacent assemblies.

- DEFICIENCIES

  - The terms "failure", "deficiency" and "non-compliant" shall be used interchangeably and shall be defined as any condition in which the installation or performance of material, system or assembly is not in compliance with the Contract Documents or manufacturer installation instructions.

  - BECxA shall maintain a BECx Action Items Log that shall contain any items that do not appear to meet the intent of the Contract Documents or manufacturer installation instructions. Digital images of non-compliant conditions shall be included. Additionally, items for potential improvement may be included on the log.

    - Deficiencies identified on the Action Items Log shall only include those items which are associated with completed installations and shall not include in-progress Work unless obvious errors are present.

  - BECxA shall update and issue the Action Item Log within two (2) business days following a site visit.  Items on the Action Item Log shall be corrected by the Constructor and building envelope Subcontractor(s) in a timely manner, and prior to Substantial Completion.  Action Items may be added to the Substantial Completion Punch List at the discretion of the Owner.

  - Costs associated with non-compliant Work shall be assigned to the Constructor.

    - Constructor’s incomplete or inaccurate Construction Checklists shall be considered cause for retesting and/or re-review by the BECxA and costs associated with retesting and re-review shall be the Constructor's expense.

    - 50% failure rate of any Functional Performance Test sampling shall be cause for retesting 100% of similar material, systems, or assemblies and shall be the Constructor's expense.

    - Non-compliant items or deficiencies identified during a BECxA review shall be considered cause for re-review by the BECxA, at the Constructor's expense. These costs shall include but not be limited to BECxA travel, re-review, re-testing, re-scheduling, or other incurred costs resulting from non-compliant items or deficiencies.

- FIRST WORKS AND MOCKUPS [Edit the highlighted sections based on the project complexity and schedule.]

  - First Works and Mockups shall be reviewed by the BECxA and Design Professional to identify and document the Work and to ensure Control Barrier integration and construction quality control measures are met.

  - The Constructor shall assemble and erect the following specified items as First Works and Mockups with specified attachment and anchorage devices, flashings, seals, and finishes for review and approval by the BECxA, Design Professional and Owner:

    - List Specified items to be reviewed as First Works and Mockups here…

  - First Works and Mockups accepted by the Owner shall be a comparison standard for remaining Work.

    - The CCxC and BECxA shall jointly identify and document the required modifications to materials, systems and assemblies associated with the First Works and Mockups.

    - First Work and Mockups shall also serve as a comparison standard for aesthetic considerations for the remaining Work.

  - First Works and Mockups to be removed before Final Completion of the Project shall remain until Substantial Completion unless otherwise directed by the Owner.

BECxA TO ENTER SAMPLE CONSTRUCTION CHECKLIST HERE

BECxA TO ENTER THE FUNCTIONAL PERFORMANCE TESTING MATRIX HERE

END OF SECTION